# SPI Mag

MODEL 282L SINGLE POINT INSERTION

ELECTROMAGNETIC FLOW METER

2” SENSOR

SUBMITTAL PACKAGE

From

McCROMETER, INC.

3255 WEST STETSON AVENUE

HEMET, CA  92545

Phone (951) 652-6811

Toll Free (800) 800-8804

Fax (951) 652-3078

www.mccrometer.com

Date:

Lit # 24510-94 Rev.1.2

| Project Name: |  |
| --- | --- |
| Purchase Order No.: |  |
| Date: |  |
| Customer Name: |  |
| Submitted By: |  |

3255 WEST STETSON AVENUE • HEMET, CALIFORNIA 92545 USA

www.mccrometer.com	                     TEL: 951-652-6811 • 800-220-2279 • FAX: 951-652-3078          Printed In The U.S.A       Lit. #24510-94  Rev. 1.2/17-10

Copyright © 2010 McCrometer, Inc. All printed material should not be changed or altered without permission of McCrometer. Any published pricing, technical data, and instructions are subject to change without notice. Contact your McCrometer representative for current pricing, technical data, and instructions.

| EQUIPMENT TO BE SUPPLIED BY McCROMETER, INC. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Part Number |  | Description |  |  |  |  | Qty |  |
| #### Model 282L |  | 2” SPI Mag Meter , “L” Series |  |  |  |  |  |  |
|  |  | Specify Pipe ID |  |  |  |  |  |  |
|  |  | (1) Converter, including: |  |  |  |  |  |  |
|  |  |  | (1) NEMA 6 Enclosure |  |  |  |  |  |
|  |  |  | (1) Three-Button Key Pad |  |  |  |  |  |
|  |  |  | (1) Back-Lit Graphical LCD Display |  |  |  |  |  |
|  |  |  | (1) Programmable Opto-Isolated Output (1) Digital Input for Batch Function Start, etc. |  |  |  |  |  |
|  |  |  | (1) 4-20mA Output for Flow (1) 90 to 265VAC @ 0.25A Input Power |  |  |  |  |  |
|  |  | (1) Electromagnetic Full Pipe Sensor including: |  |  |  |  |  |  |
|  |  |  | (20) Feet of Inter-connecting Sensor Cable |  |  |  |  |  |
|  |  |  | (1) Compression Seal |  |  |  |  |  |
|  |  |  | (1) Choice of one PVC Insertion Tube with Mounting Hardware: |  |  |  |  |  |
|  |  |  | 18” length Insert Tube Length: 24” length 30” length |  |  |  |  |  |
|  |  | (1) Instruction Manual |  |  |  |  |  |  |
| ##### Built-In Options |  |  |  |  |  |  |  |  |
|  |  | Additional Sensor Cable: |  |  |  |  |  |  |
|  |  |  | Specified Total Length: Feet |  |  |  |  |  |
| Special |  | 18 to 45 VAC/DC Input Power @ 1.6A |  |  |  |  |  |  |
| Special Special | 10 to 35 VDC Input Power @ 1.5A Stainless Steel Insertion Tube |  |  |  |  |  |  |  |
| ##### Accessories |  |  |  |  |  |  |  |  |
| 24511-13 |  | Additional Instruction Manual |  |  |  |  |  |  |
| 24510-58 |  | Additional Sensor Profiling Guide |  |  |  |  |  |  |
| 43055-2 |  | Bronze Valve/Stainless Steel Nipple |  |  |  |  |  |  |
| 43055-1 |  | Stainless Steel Valve/Stainless Steel Nipple |  |  |  |  |  |  |
| 0624B339001 |  | Sun Shield |  |  |  |  |  |  |
| 170007101 |  | Stainless Steel Tag |  |  |  |  |  |  |
| 360000701 |  | IF2 Serial Device |  |  |  |  |  |  |
| 75031 |  | Insertion Tool (Recommended for pipe ID greater than 24”) |  |  |  | FORMTEXT |  |  |

- SPI Mag™ SPECIFICATIONS

Model 282L – 2”

General

The flow meter shall consist of two components: an electromagnetic sensor and a converter for clean and wastewater.  The electromagnetic sensor shall be capable of operating in pipe diameters from 6 to 96 inches.  The flow meter shall determine the volumetric flow rate by means of the Continuity Equation where flow rate “Q” equals mean velocity “V” times cross sectional area “A” (Q = V x A).  The velocity measurement must be taken at a known location, then, through empirically established equations, the sensed velocity will be converted to a mean velocity.  The meter shall be equivalent to the SPI Mag Model 282L Single Point Insertion Electromagnetic Flow Meter as manufactured by McCrometer, Inc., in Hemet, California.

Electronics

The flow meter converter shall be microprocessor based with a keypad for instrument setup and LCD displays for totalized flow, flow rate, engineering units and velocity or totalized flow.  The converter shall power the flow-sensing element and provide a galvanically isolated 4-20mA output for flow, and one flow proportional or frequency output (transistor type) for flow rate or for external totalizer.  It shall be possible, in the test mode, to easily set the transmitter outputs to any desired value within their range.  The 4-20mA scaling, time constant, pipe size, flow proportional output, engineering units and test mode values shall be easily set via the keypad and display.  Two separate, fully programmable alarm outputs shall be provided to indicate high/low flow rates, empty pipe, fault conditions, reverse flow and over-range conditions.  The transmitter shall periodically perform self-diagnostics and display any resulting error messages.  All setup data and totalizer values may be protected by a password.

Sensor

The flow-sensing element shall be of an electromagnetic single point type design and factory calibrated to traceable standards, such as NIST.  The sensor shall be made of a polyurethane with pure carbon electrodes exposed to flow.  Installation of the sensor shall be accomplished under flowing conditions through a 2-inch valve, with final location being located near the inside wall of the flow conduit or 1/8 pipe ID.  To eliminate erroneous readings due to pipe wall effects, the sensor must have its electrodes located at least 3/16” from pipe wall and be designed with a curved tip shape, so as not to collect debris while in the operating position.  Flat tipped or Doppler sensors shall not be acceptable.

Sensor Cable

The sensor cable is 20 feet of multi-conductor, abrasive resistant, jacketed cable flexible to         -40°F.  The sensor cable shall be permanently bonded to the sensor.  Additional sensor cable, up to 300 feet, shall be available as an option.

Mounting Hardware

The insertion tube and restraining rod assembly shall be provided for the smooth installation and operation of the velocity sensor and shall be of sufficient length to allow a full profile of the flow conduit.  The optional stainless steel insertion tube shall be rated for 250 PSI @ 160o F and the PVC insertion tube shall be rated for 150 PSI @ 105 o F.  Hardware must allow sensor to be secured by bolts when sensor is being inserted and retracted.  A stainless steel compression seal shall also be supplied.

MEASUREMENT

Volumetric flow in filled flow conduits 6” (152mm) to 96” (2440 mm) in diameter utilizing insertable velocity sensor.  Flow indication in English std. or Metric units.

FLOW MEASUREMENT

Method: Electromagnetic

Accuracy: ±2% of reading ±0.03 ft/s (±0.009 m/s) zero stability from 0.3 to 20 ft/s (0.09 to 6 m/s) velocity range

Velocity Range: +0.3 to +30 ft/s (+0.09 to +9 m/s)

Has reverse flow indication.

CONDUCTIVITY

Minimum conductivity of 5μS/cm (5μmho/cm)

POWER REQUIREMENTS

AC: 90-265V 44-66 Hz (20W/25VA) or

DC: 10-35V at 20W.

AC or DC must be specified at time of ordering.

MATERIALS

Sensor:  Polyurethane exposed to flow

2” Sensor Mounting:  PVC and Stainless Steel exposed to flow.  (Stainless Steel Insertion Tube Optional)

Compression Seal:  Buna “N” exposed to flow.

OUTPUTS

Analog: 4-20mA 1000 Ohms galvanically isolated and fully programmable.

Pulse: 2 Pulse/Frequency/Alarm outputs programmable for high/low flow rates, percent of range, empty pipe, fault conditions, forward/reverse, polarity (normally open/close), analog over-range, pulse over-range, etc.

DUAL ALARMS

2 separate outputs: Isolated and protected transistor switch capable of sinking <250mA @ <35V. Note: Not isolated from frequency output. Fully programmable for high/low flow rates, % of range, empty-pipe, fault conditions, forward/reverse, polarity (normally open/close), analog over-range, pulse over-range, pulse cutoff, etc.

CONVERTER ENCLOSURE

IP67 Die cast aluminum enclosure

5.75” H x 5.75” W x 6.69” D

(14.6 cm H x 14.6 cm W  x 17 cm D ).  Weight:  6.8 lbs. (3.1 kg)

ELECTRICAL CONNECTIONS

Compression gland seals for 0.125” to 0.375” dia. round cable.

ISOLATION

Galvanic separation to 50VDC between analog, pulse/alarm, and earth/ground.

STANDARDS

CE Certified (Converter only)

ENVIRONMENTAL

Pressure/Temperature Limits:

PVC Insertion Tube:

Up to 105°F (41°C) at 150 psi

Stainless Steel Insertion Tube:

Up to 160°F (71°C) at 250 psi

(McCrometer recommends the use of Stainless Steel)

Electronics: Operating and storage temperature: -4° to 140°F (-20°C to +60°C)

KEYPAD AND DISPLAY

Can be used to access and change all set-up parameters using three membrane keys and LCD display.

OPTIONS

DC Power

Pole mounting kit

Sun shield

Sensor insertion tool

Stainless steel ID tag

Valves

Additional sensor cable up to 300’ (for longer lengths, consult factory)

Sun Shield (Optional)

Installation Tool – Specialized sensor insertion tool used for installation, profiling and maintenance of the sensor (optional).

SPI Mag 282L 2” Meter Technical Information

SPI Mag Parts Description

SPI Mag 282L 2” Electrical Cable Connections